## bmHPCrawData
atlasPartsId | 20220170200092
manufacturerSerialNo | SP0286
eventDescription | PC_HYBRID
date [dd/mm/yyyy] | 14/05/2002
location [instituteCode(DB)] | 017
personInitial | YU
problem [YES/NO] | NO
pass [YES/NO] | YES
comments
C1~C28 capacitorsLotID | IA1D10J39
C51~C58 capacitorsLotID | IA1N29M26
C71~C75 HV capacitorsLotID | IA9015Y11
R27~R30 resitorsLotID | C9Y0401
R33~R34 resitorsLotID | CQX2913
R35 resitorsLotID | NQX0857
TM1~TM2 thermistersLotID | 0013
CON connectorLotID | 1
FLEX_CIRCUIT LotID | 93272751 016-005
PA pitch adaptorsLotID | 1
CC carbon-carbon bridgesLotID | 3ND.20020124
Conductive epoxyLotID | 0221011
Thermal epoxyLotID | 1225011
solderBallLotID | SS029304
solderReelLotID | 01.12.27
FLEX_CIRCUIT visual inspection[G/NG] | G
Integrity test of lines [G/NG] | G
dateCCbridge attaching [dd/mm/yyyy] | 14/05/2002
visual inspection [G/NG] | G
Thickness Link0 (<0.65) | 0.621
Thickness Link1 (<0.65) | 0.609666666666667
Bow (long) Link0 (< 0.075) | 0.042475
Bow (long) Link1 (< 0.075) | 0.03654
Bow (across) Link0 (< 0.075) | 0.067315
Bow (across) Link1 (< 0.075) | 0.066995
Twist Link0 (<0.1) | -0.02398
Twist Link1 (<0.1) | -3.20666666666667E-03
dateComponent soldering [dd/mm/yyyy] | 16/05/2002
visual inspection [G/NG] | G
number of Wirebond-Pull on PC hybrid | 4
average (>6.0gr) | 7.18
range(max-min) [gr] | 0.52
min [gr] | 6.84
datePitchAdaptor attaching [dd/mm/yyyy] | 17/05/2002
visual inspection [G/NG] | G
number of Wirebond-Pull on PA (Lot) | 4
average (>6.0gr) | 9.19
range(max-min) [gr] | 0.87
min [gr] | 8.47
Capacitance Vcc-GND (microF) at 1KHz (4.0<X<4.8) | 11.51
Capacitance Vdd-GND (microF) at 1KHz (4.0<X<4.8) | 11.71
Impedance HV-GND (kOhm) at 100Hz ( 30<X< 36) | 32.10
Impedance HV-GND (kOhm) at 1KHz ( 9<X< 11) | 9.93
Impedance HV-GND (kOhm) at 10KHz (5.7<X<7.7) | 6.65
Impedance HV-GND (kOhm) at 100KHz (5.0<X<7.1) | 6.23
Resistance R27 (Ohm) ( 99<X<101) | 100.18
Resistance R28 (Ohm) ( 99<X<101) | 100.20
Resistance R29 (Ohm) ( 99<X<101) | 100.07
Resistance R30 (Ohm) ( 99<X<101) | 100.09
Resistance TM1 (kOhm) at 25 deg.C. ( 9.8<X<10.2) | 9.99
Resistance TM2 (kOhm) at 25 deg.C. ( 9.8<X<10.2) | 10.06
LV leakage current for Icc (nA) at 10V (X<10) | 45.49
LV leakage current for Idd (nA) at 10V (X<10) | 47.59
HV leakge current (nA) at 500V (X<10) | 6.49
dateTC [dd/mm/yyyy] | 29/05/2002
TC loTemperature [C]
TC hiTemperature [C]
TC repetition
visual inspection [G/NG] | G
Thickness Link0 (<0.65) | 0.621666666666667
Thickness Link1 (<0.65) | 0.609333333333333
Bow (long) Link0 (< 0.075) | 0.039835
Bow (long) Link1 (< 0.075) | 0.03396
Bow (across) Link0 (< 0.075) | 0.07532
Bow (across) Link1 (< 0.075) | 0.072985
Twist Link0 (<0.1) | -5.15466666666667E-02
Twist Link1 (<0.1) | 3.23933333333333E-02
Capacitance Vcc-GND (microF) at 1KHz (4.0<X<4.8) | 11.35
Capacitance Vdd-GND (microF) at 1KHz (4.0<X<4.8) | 11.54
Impedance HV-GND (kOhm) at 100Hz ( 30<X< 36) | 32.60
Impedance HV-GND (kOhm) at 1KHz ( 9<X< 11) | 9.95
Impedance HV-GND (kOhm) at 10KHz (5.7<X<7.7) | 6.65
Impedance HV-GND (kOhm) at 100KHz (5.0<X<7.1) | 6.20
Resistance R27 (Ohm) ( 99<X<101) | 100.18
Resistance R28 (Ohm) ( 99<X<101) | 100.20
Resistance R29 (Ohm) ( 99<X<101) | 100.08
Resistance R30 (Ohm) ( 99<X<101) | 100.09
Resistance TM1 (kOhm) at 25 deg.C. ( 9.8<X<10.2) | 9.97
Resistance TM2 (kOhm) at 25 deg.C. ( 9.8<X<10.2) | 10.03
LV leakage current for Icc (nA) at 10V (X<10) | 48.74
LV leakage current for Idd (nA) at 10V (X<10) | 47.73
HV leakge current (nA) at 500V (X<10) | 6.68
visual inspection [G/NG] | G
Height of Component C73 | 2.2
Height of Component C53 | 2.33
Height of Component C54 | 2.34
Height of Component C74 | 2.2
Height of Component C55 | 2.34
Height of Component C56 | 2.35