## bmHPCrawData
atlasPartsId | 20220330200017
manufacturerSerialNo | SP0382
eventDescription | PC_HYBRID
date [dd/mm/yyyy] | 17/06/2002
location [instituteCode(DB)] | 017
personInitial | YU
problem [YES/NO] | NO
pass [YES/NO] | YES
comments
C1~C28 capacitorsLotID | IA1D10J39
C51~C58 capacitorsLotID | IA1N29M26
C71~C75 HV capacitorsLotID | IA9015Y11
R27~R30 resitorsLotID | C9Y0401
R33~R34 resitorsLotID | CQX2913
R35 resitorsLotID | NQX0857
TM1~TM2 thermistersLotID | 0013
CON connectorLotID | 1
FLEX_CIRCUIT LotID | 93272751 016-006
PA pitch adaptorsLotID | 2
CC carbon-carbon bridgesLotID | 3ND.20020124
Conductive epoxyLotID | 0221011
Thermal epoxyLotID | 1225011
solderBallLotID | SS029304
solderReelLotID | 01.12.27
FLEX_CIRCUIT visual inspection[G/NG] | G
Integrity test of lines [G/NG] | G
dateCCbridge attaching [dd/mm/yyyy] | 17/06/2002
visual inspection [G/NG] | G
Thickness Link0 (<0.65) | 0.628
Thickness Link1 (<0.65) | 0.625
Bow (long) Link0 (< 0.075) | -0.062
Bow (long) Link1 (< 0.075) | -0.0265
Bow (across) Link0 (< 0.075) | -0.0425
Bow (across) Link1 (< 0.075) | -0.032
Twist Link0 (<0.1) | 0.075
Twist Link1 (<0.1) | 0.009
dateComponent soldering [dd/mm/yyyy] | 19/06/2002
visual inspection [G/NG] | G
number of Wirebond-Pull on PC hybrid | 4
average (>6.0gr) | 8.44
range(max-min) [gr] | 1.89
min [gr] | 7.44
datePitchAdaptor attaching [dd/mm/yyyy] | 20/06/2002
visual inspection [G/NG] | G
number of Wirebond-Pull on PA (Lot) | 10
average (>6.0gr) | 9.09
range(max-min) [gr] | 1.53
min [gr] | 8.49
Capacitance Vcc-GND (microF) at 1KHz (4.0<X<4.8) | 11.60
Capacitance Vdd-GND (microF) at 1KHz (4.0<X<4.8) | 11.64
Impedance HV-GND (kOhm) at 100Hz ( 30<X< 36) | 30.40
Impedance HV-GND (kOhm) at 1KHz ( 9<X< 11) | 9.87
Impedance HV-GND (kOhm) at 10KHz (5.7<X<7.7) | 6.62
Impedance HV-GND (kOhm) at 100KHz (5.0<X<7.1) | 6.21
Resistance R27 (Ohm) ( 99<X<101) | 100.23
Resistance R28 (Ohm) ( 99<X<101) | 100.19
Resistance R29 (Ohm) ( 99<X<101) | 100.18
Resistance R30 (Ohm) ( 99<X<101) | 100.17
Resistance TM1 (kOhm) at 25 deg.C. ( 9.8<X<10.2) | 10.09
Resistance TM2 (kOhm) at 25 deg.C. ( 9.8<X<10.2) | 9.83
LV leakage current for Icc (nA) at 10V (X<10) | 48.42
LV leakage current for Idd (nA) at 10V (X<10) | 47.20
HV leakge current (nA) at 500V (X<10) | -119.25
dateTC [dd/mm/yyyy] | 26/06/2002
TC loTemperature [C]
TC hiTemperature [C]
TC repetition
visual inspection [G/NG] | G
Thickness Link0 (<0.65) | 0.638
Thickness Link1 (<0.65) | 0.631
Bow (long) Link0 (< 0.075) | -0.068
Bow (long) Link1 (< 0.075) | -0.033
Bow (across) Link0 (< 0.075) | -0.0535
Bow (across) Link1 (< 0.075) | -0.0345
Twist Link0 (<0.1) | 0.072
Twist Link1 (<0.1) | 0.004
Capacitance Vcc-GND (microF) at 1KHz (4.0<X<4.8) | 11.46
Capacitance Vdd-GND (microF) at 1KHz (4.0<X<4.8) | 11.49
Impedance HV-GND (kOhm) at 100Hz ( 30<X< 36) | 30.80
Impedance HV-GND (kOhm) at 1KHz ( 9<X< 11) | 9.89
Impedance HV-GND (kOhm) at 10KHz (5.7<X<7.7) | 6.63
Impedance HV-GND (kOhm) at 100KHz (5.0<X<7.1) | 6.21
Resistance R27 (Ohm) ( 99<X<101) | 100.23
Resistance R28 (Ohm) ( 99<X<101) | 100.19
Resistance R29 (Ohm) ( 99<X<101) | 100.18
Resistance R30 (Ohm) ( 99<X<101) | 100.17
Resistance TM1 (kOhm) at 25 deg.C. ( 9.8<X<10.2) | 10.10
Resistance TM2 (kOhm) at 25 deg.C. ( 9.8<X<10.2) | 9.84
LV leakage current for Icc (nA) at 10V (X<10) | 48.02
LV leakage current for Idd (nA) at 10V (X<10) | 47.76
HV leakge current (nA) at 500V (X<10) | 8.71
visual inspection [G/NG] | G
Height of Component C73 | 2.250
Height of Component C53 | 2.365
Height of Component C54 | 2.362
Height of Component C74 | 2.228
Height of Component C55 | 2.368
Height of Component C56 | 2.357